## Sheet1
Enter a cable gauge, cable run length, speaker voltage and tapping, and check the power dissipated in the cable run. Results provided at full and 1/3 (mild abuse) levels, for Copper and Aluminium wire
AWG | Diameter (mm) | Area (mm2) | Resistance, Copper, ohms/1000m | Resistance, Aluminium, ohms/1000m |  | Inputs
40 | 0.08 | 0.005 | 3448 | 5300 | Gauge: | 16 | AWG
39 | 0.09 | 0.0064 | 2693 | 4141 | Distance to speaker: | 250 | m
38 | 0.1 | 0.0078 | 2210 | 3397 | Line voltage: | 100 | V |  | Full power results (Copper) |  | 1/3 power results (Copper)
37 | 0.11 | 0.0095 | 1810 | 2789 | Total Speaker tapping: | 125 | W |  |  |  | 41.6667 | W
36 | 0.13 | 0.013 | 1326 | 2038
35 | 0.14 | 0.015 | 1120 | 1767 | Load impedance: | 80 | ohms | Current in cable: | 1.25 | A | 0.41667 | A
34 | 0.16 | 0.02 | 862 | 1325 | Copper R % of load: | 8.125 | % | Power loss in cable: | 10.1562 | W | 1.1285 | W
33 | 0.18 | 0.026 | 663 | 1019 | Aluminium R % of load: | 12.5 | %
32 | 0.2 | 0.031 | 556 | 855 | (Rule of thumb: <= 5%)
30 | 0.25 | 0.049 | 352 | 541
28 | 0.33 | 0.08 | 216 | 331 |  |  |  |  | Full power results (Aluminium) |  | 1/3 power results (Aluminium)
27 | 0.36 | 0.096 | 180 | 276 | [6 empty] | 41.6667 | W
26 | 0.41 | 0.13 | 133 | 204
25 | 0.45 | 0.16 | 108 | 166 |  |  |  | Current in cable: | 1.25 | A | 0.41667 | A
24 | 0.51 | 0.2 | 88 | 133 |  |  |  | Power loss in cable: | 15.625 | W | 1.7361 | W
22 | 0.64 | 0.33 | 52 | 80
20 | 0.81 | 0.5 | 34 | 53
18 | 1 | 0.82 | 21 | 32
16 | 1.3 | 1.3 | 13 | 20
14 | 1.6 | 2.1 | 8.2 | 13
13 | 1.8 | 2.6 | 6.6 | 10
12 | 2.1 | 3.3 | 5.2 | 8
10 | 2.6 | 5.3 | 3.3 | 5
8 | 3.3 | 8.3 | 2.1 | 3.2
6 | 4.1 | 13.3 | 1.3 | 2
4 | 5.2 | 21.2 | 0.81 | 1.3
3 | 5.83 | 26.7 | 0.65 | 0.99
2 | 6.5 | 33.6 | 0.51 | 0.79
1 | 7.4 | 42.4 | 0.41 | 0.63
Copper |  |  | Alu
Ohms/1000m | 13 |  | 20
Ohms | 6.5 |  | 10 | [6 empty] | 2021-01-28 |  | TN-029